## Slide 1: Lessons Learned Implementing an IEC 61850-based Microgrid Power-Management System
Presented by: Jared Mraz, P.E.
October 12, 2015

## Slide 2: Introduction
Fuel refinery in Salt Lake City, Utah
Reliability improvement projects started in 2012
  New main substation
  New medium-voltage distribution infrastructure
  New microprocessor-based relays installed
  Dedicated Protection and SCADA network installed
Existing loads cut-over from aging substations to new feeds

## Slide 3: System Overview

## Slide 4: Need for Power Management System
Plant load 18 MW prior to upgrades
Several expansion projects executed during course of reliability improvements
By cutover in March 2015, load grew to 25 MW
  Generators capable of 18.4 – 24 MW
  Utility source provides balance
Load shedding scheme required to keep Co-Gens running during islanding
  Loss of Co-Gens results in costly outage due to loss of steam

## Slide 5: Power Management System Overview
Contingency-based scheme
  Central controller monitors system conditions
  Controller calculates amount to shed in real-time for pre-defined “contingencies”
  Requires protection-speed communications
    Met performance requirements identified during preliminary studies
  Protection network already in place for GOOSE schemes at plant
  GOOSE selected as protocol for load shedding

## Slide 6: Contingency Scheme Overview
Three Breaker Types
  Contingency
    Change of state can initiate load shed
    Monitor status and power import
  Topology
    Status used to determine system configuration
  Load
    Monitor power consumption
    Tripped during load shedding event

## Slide 7: Contingency-based Scheme Example
Shed load when both main breakers open
Shed pre-event import plus margin
Decisions based on real-time metering and breaker status from field devices

## Slide 8: Contingency-based Scheme Example
Scheme must shed 4 MW, plus small margin
Lowest-priority 5 MW feeder selected to trip
Controller will trip feeder if contingency trigger occurs

## Slide 9: Contingency-based Scheme Example
Main breakers trip for utility undervoltage

## Slide 10: Contingency-based Scheme Example
Pre-selected feeder tripped by controller

## Slide 11: Testing Approach
Bench Test
  RTDS testing selected due to complexity and criticality of system
  Allowed for thorough closed-loop testing
  Allowed scheme controllers and IEDs to be interfaced with test system
Site Acceptance Test
  Communications checks
  Limited set of functional tests
  Islanding events during plant outage with simulated load

## Slide 12: Lesson 1 – Accurately Characterize the System
Generator dynamic model validation
System modeled in phasor domain software
Determined performance requirements for power management system
Limit assumptions about system parameters
Increased confidence in model

## Slide 13: Lesson 2 – Thoroughly Test System Operating Modes
Accurately model plant and nearby utility system
Examine normal and contingency cases
Existing and future loading
Variety of initiating conditions for islanding events
Determine controlling cases
Scheme performance for all cases verified with RTDS
  Focus on controlling cases

## Slide 14: Lesson 3 – Include at Least One of Each Device Type in the Bench Test
Actual relays and controllers
Contingency and load breaker relays
Problem with GOOSE analog values
  Required re-design of frequency-based triggers
Problem may not have been identified using traditional bench test method

## Slide 15: Lesson 4 – Test System Failure Modes
Verify scheme operation during failure modes
  Unintended operations not tolerated
Failure modes considered
  Communications failure
  Settings changes
  Loss of IED power
Failure mode testing
  Security issue identified in controllers during re-establishment of communications
  52A status issue uncovered during DC power failures

## Slide 16: Lesson 5 – Identify FAT and Commissioning Test Boundaries
Factory Acceptance Test
  Realistic testing in consequence-free environment
  Not impacted by operational restrictions or outage duration
  Response of entire system viewed by design team
  Test power management system for all foreseeable contingencies
  Verify logic of controller and each unique IED type in system
  Minimize exposure to field changes

## Slide 17: Lesson 5 – Identify FAT and Commissioning Test Boundaries (Continued)
Site Acceptance Test
  Keep testing succinct to limit outage duration
  Live islanding tests not practical
  Focus on items not verified in lab
    Communications checks
    I/O, controls, and alarm verifications

## Slide 18: Lesson 6 – Carefully Preserve System Test Details
Bench Test Setup
  RSCAD Model, Photos of Setup, Wiring Diagrams
  Allows test environment to be recreated
Bench Test Results
  COMTRADE captures from RTDS
  Device SERs captured for all tests
  Automated tests for controller logic
Site Acceptance Results
  Device SERs and relay event reports captured
Test results provide a known reference point for comparison with actual field events.

## Slide 19: Conclusions
IEC61850 GOOSE messaging provides flexibility for protection and control systems
  Protection-class network required
RTDS testing provides thorough performance validation
Thorough lab testing for complex systems minimizes field changes and improves final product

## Slide 20: Questions?