## Slide 1: Harmonic Issues of AEP Welsh HVDC System Bob Malek Kiril Andov Richard Gutman Ben Mehraban 10/12/2015

## Slide 2: Power Quality Challenges in Transmission Grid
  Rapid Growth of Digital Electronics in Distribution System
    Harmonics enter transmission network
    Risk of resonance
    Rising levels of background harmonics (in systems with low fault levels)
    Equipment outages and degraded equipment life
    Overloading of harmonic filters located in the grid, and malfunction of protective devices.
  “suppressing harmonics in transmission grids has become significantly more important to help ensure trouble-free operation by electric utilities.”

## Slide 3: Welsh HVDC System
(ERCOT)
(SPP)

## Slide 4: Operation Issues
  During the last five years, the converter station has experienced some operational Issues especially when all three Monticello generating units are offline:
    Measuring and protection equipment malfunction
    Overloading of harmonic filters: The filter bank current has an unusually high 5th harmonic component
    The HVDC control system will trip the tie operation when no filters are available.
  Elevated 5th harmonic currents
    Can cause thermal damage to the filter components, in particular the reactors of the filters.
    The cause of the 5th harmonic current is related to higher than normal system voltages, light loading of the transmission grid and certain system configurations that create a weak system.
    The origin of the ambient 5th order harmonic is unknown, but is thought to be related to semiconductor switching consumer loads, such as computer power supplies and industrial/commercial operations.

## Slide 5: Emergence of Power Quality Concerns
  Voltage Issues
    Voltage problems on the ERCOT (Monticello) side since 1995.
    The converter station was designed for a nominal voltage range of 328 kV to 362 kV. Oncor, in an attempt to boost the voltage in Dallas/Fort Worth area, operates the Monticello bus at high voltages (Maximum of 355 kV).
    This can result in an even higher voltage on the HVDC bus due to the combination of high voltage at Monticello, light loading of the transmission system, filter operation and active power transfer level of the converter.
    The high voltage can be counteracted to some extent by the converter controls. The converter can change the firing angle to consume more reactive power and lower the voltage, provided there are sufficient margins in the firing angle operating range.
    At low power transfers (below 100 MW), the firing angle is very close to its upper limit leaving no margin for voltage control. The high AC voltage can cause the following issues:
      reduced life of switchyard equipment;
      suboptimal efficiency operation;
      filter overload/tripping and the HVDC tie shut down.
Notes: The voltage issues are most prominent in the months of February to May. A lightly loaded transmission system changes the ratio of line capacitance to load inductance. Under certain conditions, the combination of line capacitance of the 16-mile transmission line connecting Monticello Station to Welsh HVDC and the capacitance of the filter banks causes the bus voltage at the converter station to rise as much as 6 kV above that of the Monticello bus.

## Slide 6: Emergence of Power Quality Concerns
  Harmonic Issues
    Elevated 5th harmonic currents have been observed in the filter banks under the same conditions that result in high bus voltage.
    The issues appear to be magnified at higher voltage levels when one or more transmission lines, or generating units, are out of service and the AC system is weakened. The additional harmonic current added to the fundamental current can exceed the trip set point on the filter overcurrent relays.
    To mitigate the problems
      alarms were installed to alert the dispatchers when the HVDC tie goes into “Voltage Limit Control”.
      The switching point of the second filter bank was raised to help keep the bus voltage from rising by forcing the VAR exchange with the transmission system to be more inductive.
      AEP initiated an extensive analysis to address the issues permanently.
Notes: Filter banks are designed to be a low impedance path to ground for the 11th, 13th, 23rd and 25th harmonics. These are characteristic harmonics generated by thyristor switching in the converter bridge [2], [3]. The filters are tuned broad enough to provide a low impedance path for the 5th harmonic.

## Slide 7: Harmonic Measurement
  Harmonic Measurements
    field harmonic measurements were done during a span of two years.
    power quality recording equipment was setup on both terminals of the tie.
    Recorded data was used to track trends of individual low order harmonics, determine if high levels of distortions can be correlated with switching of local or remote equipment.
    Correlation of high distortion levels with switching of local or remote equipment posed as a challenging task to the team because of the fact that AEP doesn’t own a majority of the network on both sides
Harmonic order | ERCOT side (%) | SPP side (%)
3rd | 1.02 | 0.37
5th | 3.64 | 2.17
7th | 1.19 | 0.53
9th | 0.18 | 0.20
11th | 0.44 | 0.18
Applied Low Order Harmonic Distortion Levels

## Slide 8: Analysis and Studies
  Analysis and Performance Criteria
    Due to the proprietary nature of the generator model data in the vicinity of the HVDC tie, the system characteristics on both sides of the HVDC terminals were used in a form of harmonic impedance as a function of frequency for various system topologies.
    Extensive PSCAD simulation was setup to calculate the network impedance as seen from the HVDC terminals, in which critical equipment was identified and placed in a list.
    A custom PSCAD component was created to cycle through the list and arrange all of the possible combinations for the network topology as shown in Figure below.

## Slide 9: Performance and Criteria
  IEEE 519
  Meeting of the harmonic distortion limits specified in IEEE Standard 519 was challenging
    It was decided to rate the internal components of the low order filter to withstand higher levels of distortion and mandate performance compliance to the limits specified in IEEE 519 only to the characteristic harmonics and make sure that any combination of the shunt branches connected to either side of the HVDC terminal can reliably operate

## Slide 10: Design of the low order filter
  Additional shunt reactors were required to lower the voltage
Notes: To design and install a low order filter to assist existing filters in conditions with elevated low order harmonic distortions and to compensate the reactive power of the low order filter, additional shunt reactors were required on both sides of the tie to help with voltage regulation at the HVDC terminals, when nearby conventional generation is offline. Figure 4. illustrates the final layout of the filter branches and shunt reactor branches, and which was used as a base for calculation of voltage magnification by low order background harmonic sources.

## Slide 11: Design of the low order filter
Notes: High level overview of the design workflow is illustrated in Figure 5. From Figure 5. it can be seen that the input data for the low order filter design and performance evaluation is the voltage distortion as defined in 3.1 and Zsystem as outlined in 3.2.1, which is fed into the filter design engine. At this stage, amplification factors are calculated for various filter branch and reactor branch configurations, as well as current distributions for the low order filter internal components. Then the results are passed to the performance criteria block, which determines if the performance criterion is met. If the outcome is “Yes,” then the design can be considered final. If “No,” then the internal components of the low order filter are adjusted and looped through the filter design and performance evaluation block.

## Slide 12: Design of the low order filter
Notes: Figure 6 shows the single line diagram of the additional new Low Order Filters which are double tuned high pass damped filters each rated 100 MVar tuned to 5th/11th harmonic. The rating of the ac filter components are mainly determined by the high magnitudes of low order harmonics n = 3, 5, 7 and 9. It should be noted that the more severe harmonic impedances require higher energy ratings for the ERCOT side.
The additional tuning for 11th harmonic is needed since a reduced damping of HVDC converter harmonics is observed for the new harmonic network impedances adapted to recent changes in the topology of the AC systems.

## Slide 13: Conclusion
  Severe challenges that are imposed by amplified background harmonics for AEP Welsh HVDC operation under certain weak system conditions can cause amplification of ambient harmonics to intolerable levels.
  It is important to implement an efficient process to perform the necessary measurements, studies and analysis to mitigate the issue and design additional harmonic filters and/or shunt reactors.
  In the Welsh HVDC project, all system contingencies were considered with the worst (highest) ambient harmonics measurements to design the filters.
  This approach provides a robust and reliable design that maintains the harmonic levels within operable limits under all system conditions
  Growth in future under similar uncertainties.